Bangladesh University of Engineering & Technology

Department: EEE

Level/Term: 4-2

Course: EEE 414

Course Title: Electrical Services Design

Project: Electrical Design of a Residential Building

IDs: 1806099, 1806101, 1806102, 1806105, 1806107, 1806125

Names:

Mahin Shahriar

Niaz Mahmud

Soumik Shanto

Ihzaz Abrar Sadik

Priya Acharjee

Arnab Nath

Introduction

The electrical design is equally important as the structural one while construction of a building, for safe, comfortable & efficient operation of the users. There are several rules, regulations & standards, both local & internationally recognized. A good design must maintain these. In our project, we have demonstrated the electrical design of such a residential building.

Building Specifications

The building as a reference we used was a ten-floor building, with a basement for accommodating the parking needs of the residents. Each floor consisted of two equally built units. There was a lift and other necessary features installed for convenience. The maximum length of the building is 67’-6” & maximum width is 50’-3”. The roof has necessary lightning protection installed for safety.

Layouts

Basement

Ground Floor

Roof

First Floor

Electrical Calculations

Master Bedroom:

Area = 12’-8” x 10’-8”

= 135.111 ft2

= 12.5522 m2

Let, Standard Luminance of the bedroom = 150 lux

Loss factor, LLf = 0.9 (assumed)

Utilization factor = 0.5 (as the bulb will be connected to wall)

We will use a 15W bulb which has standard luminance of 1500 lux

So, Bulb needed = E*AreaF*UF*LLf = 150*12.55211500*0.5*0.9

= 2.7893

So, we will use 2 pcs of 15W LED bulbs and 1 pc of 10W ceiling light bulbs.

Fan needed = 135.111100 = 1.3511

So, 1 fan is needed.

Bedroom-2(upper left):

Area = 10’-8” x 9’-6”

= 101.3365 ft2

= 9.4144 m2

Bulb needed = E*AreaF*UF*LLf = 150*9.41441500*0.5*0.9

= 2.04

So, we will use 2 pcs of 15W LED bulb

Fan needed = 101.335100 = 1.01335

So, 1 fan is needed.

As per Master Bedroom 1, the circuit breaker of 15A is needed

Bedroom-3(upper right):

Area = 9’-6” x 10’

= 95 ft2

= 8.82579 m2

Bulb needed = E*AreaF*UF*LLf = 150*8.82571500*0.5*0.9

= 1.9612

So, we will use 2 pcs of 15W LED bulb

Fan needed = 95100 = 0.95

So, 1 fan needed.

Bedroom-4(Bottom-right):

Area = 12’-10” x 14’

= 179.2 ft2

= 16.64 m2

#Bulb needed = E*AreaF*UF*LLf = 150*16.641500*0.5*0.9

= 3.69

So, we will use 3 pcs of 15W LED bulb and a 10W ceiling light.

Fan needed = 179.2100 = 1.792

So, 1 fan needed.

Toilet:

Area = 4’-8” x 7’-3’’

= 33.83 ft2

= 3.1429 m2

#Bulb needed = E*AreaF*UF*LLf = 100*3.1429900*0.5*0.9 [100 lux for toilet]

= 0.8730

So, we will use 1 pc of 10W LED (900 lumen)

Also 1 exhaust fan.

Bulb and Exhaust fan  100W

Hair Dryer,Heater + other safety factor  1000W

Total = 1100W

P = VI

- I = 1100220A = 5A

So, 5A circuit breaker with 1.5mm2	fuse.

Kitchen:

Area = 7’-4” x 6’-6’’

= 47.6645 ft2

= 4.428 m2

#Bulb needed = E*AreaF*UF*LLf = 200*4.4281500*0.5*0.9	        [200 lux for toilet]

= 1.32

So, we will use 1 pc of 15W LED & 1 pc of ceiling bulb

Stairs:

Area = 8’-6” x 15’-6’’

= 131.755 ft2

= 12.2399 m2

#Bulb needed = E*AreaF*UF*LLf = 100*12.2399900*0.7*0.9	     [100 lux for stairs][UF = 0.7]

= 2.1587

So, we will need 2 pcs of ceiling LED bulb

Corridor:

Area = 12’ x 3’-9’’

= 45 ft2

= 4.18 m2

#Bulb needed = E*AreaF*UF*LLf = 100*4.18900*0.5*0.9	[100 lux for stairs][UF = 0.7]

= 1.03

So, we will need 1 pc of 10W LED bulb

Drawing Room:

Area = 24’ x 10”

= 240 ft2

= 22.2967 m2

#Bulb needed = E*AreaF*UF*LLf = 150*22.29671500*0.5*0.9	     [150 lux for dinning table]

= 4.9548

So, we will need 5 pcs of 15W LED bulb

Fan needed = 240100 = 2.4

So, 2 fan needed.

Ground Floor (SB Calc.)

For SB1

F1 and L5 are used, L6 also used.

F1  100W

L5  15W

L6  15W

P = 130W.

I = 130220*0.7A = 0.8441 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

For SB2

1x1.5 rm BYM + 1.5 BYA ECC are used.

For SB3

WL 10W

CL  10W

EF  40W

P = (10+40+10+10+10+10+10) W.

= 100W

I = 100220*0.7A = 0.6493 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

For SB4:

P = (5x10)W.

= 50W

I = 50220*0.7A = 0.3246 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

For SB5:

P = (2x10) W.

= 120W

I = 120220*0.7A = 0.77922 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

Ground Floor (SDB Calc.)

For SDB:

P = (130+100+50+120) W

= 400W

I = 400220*0.7A = 2.597 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

Ground Floor (Emergency Calc.)

For ESB1

As L1 ,L2 are fluorescent LED

P = (15+15) = 30W

I = 30220*0.7 = 0.1948 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

For ESB2

As L3 ,L4 are fluorescent LED

P = (15+15) = 30W

I = 30220*0.7 = 0.1948 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

For ESB3

I = ESB1+ESB2220*0.7 = 60220*0.7 = 0.3896 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

1st Floor (SB calculation)

SB2

L6 15W

FL  100W

WL3, CL3  10W

2 pin Socket  100W

P = (15+100+10+10+100) W.

= 235W

I = 235220*0.7A = 1.5259 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used

SB3

L1, L2, L3, L415W

F3, F4100W

3 pin P socket  3000W

3 pin Q socket4000W

2 pin Socket 100W

P = (4x15) + (2x100) + 100+ 175 W

= 535 W

I = 535220*0.7A = 3.474 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used

SB4

L815W

WL10W

EF40W

2 pin Socket 100W

P = (15+10+40+10 +100) W

= 175 W

I = 175220*0.7A = 1.136 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used

SB5

L9, L1015W

F6100W

EF240W

WL410W

2 pin Socket 100W

P = (2x15+100+40+10+100) W

= 280 W

I = 280220*0.7A = 1.8181 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

SB6

EF240W

WL410W

P = (40+10) W

= 50W

I = 50220*0.7A = 0.3246 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

SB7

L1315W

P = (15+280) W

= 295W

I = 295220*0.7A = 1.9155 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

SB8

L11, L1215W

F5100W

2 pin Socket 100W

P = (2x15+100+50+100) W

= 280 W

I = 280220*0.7A = 1.8181 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

SB9

EF340W

WL510W

P = (10+40) W= 50 W

I = 50220*0.7A = 0.324 A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

1st Floor (SDB Calc.)

SDB1

Total Load = SB2+ SB3+ SB5+ SB7

= (235+535+280+295) W

= 1345 W

SDB Load = 1345×0.7+6×3000×0.2 = 4541.5 W

SDB Current =4541.5220*0.7A = 29.49 A

So, 40A MCCB is needed from SDB to MDB.

1st Floor (Emergency Calc.)

ESB1

L515W

2 pin Socket100W

P = (15+100) W

= 115 W

I = 115220*0.7A = 0.7467A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

ESB2

L715W

F2 100W

P = (15+100) W

= 115 W

I = 115220*0.7A = 0.75A

So, 2x1.5 rm BYM + 1.5 BYA ECC are used.

ESDB1

Total Load = (115+115) W= 230 W

3 pin Socket =3000 W

I = 230*0.7+3000*0.2220*0.7A = 4.94A

ESB3

I = 115220*0.7A = 0.7467A

ESB4

I = 0.75A

ESDB2

Total Load = (115+115) W= 230 W

3 pin Socket =3000 W

I = 230*0.7+3000*0.2220*0.7A = 4.94A

Electrical Components & Wiring

Basement

Ground Floor

Roof

First Floor

Switch Board Diagrams

Basement

Ground Floor

First Floor

Emergency Switch Board Diagrams

Ground Floor

First Floor

Discussion

The crossing of conduits in the drawing was avoided as much as possible. For the few crossings that may seem to occur, they can be passed through separate channels of varying length of the walls. Also, the customized conduits, C10, C11 & C15 are required due to load exceeding the conduit ratings provided in lab sheet. In case of these conduits, they comply with the conduit characteristic chart provided.